## Table 1
Tubular ring cable lugs, KOR type

## Table 2
FEATURES & BENEFITS
ring cable lug Cu, standard, with galvanic tin plating
description of cable cross-section and cable lug size on palm surface
for voltage below 1 kV acc. to EN IEC 61238-1-1:2019 for the voltage range 1-36 kV acc. to EN IEC 61238-1-3:2019
positive result of tests for compliance with the standard for round Cu conductors of Class 2

## Table 3
MECHANICAL DATA
Material | Cu
Surface | tin-plated

## Table 4
CERTIFICATES & STANDARDS
Standards | EN IEC 61238-1-1:2019 EN IEC 61238-1-3:2019 - mechanical strength Class 1 - short-circuit resistance Class A for range of rated cross-section 25-240mm²
UL certificate | E475284 (according to table in the technical data sheet)
Design | standard
Świadectwo uznania typu PRS | TE/1137/880567/25

## Table 5
NOTE! Sector-shaped conductors (sm) must be rounded with special dies. For crimping cable lugs on cables of 5 class conductors (from cross-section of 10 mm²), we recommend crimping in a “hexagon with fangs” using KP22-FL type dies. UL certificate - visit www.ergom.com

## Table 6
Type | Index Ergom | Cross-section, rm/sm [mm²] | d | D | a | c1 | c2 | E | W | Screw hole | UL | Socket code no. - 2 class | Socket code no. - 5 class | Lz/s | Lz/w | Quantity in package [pcs] | Weight [kg]
KOR 0,75/3 (100 PCS) | E11KM-01020100150 | 0.75 | 1.3 | 2.8 | 5.8 | 3.25 | 3.8 | 12 | 6 | M3 | √ | - | - | - | 1 | 100 | 0.06
KOR 0,75/4 (100 PCS) | E11KM-01020100250 |  |  |  |  | 4 | 4.8 | 13 | 6.5 | M4
KOR 0,75/5 (100 PCS) | E11KM-01020100350 |  |  |  |  | 4.75 | 5.3 | 14 | 7.5 | M5
KOR 1,5/3 (100 PCS) | E11KM-01020100450 | 1.5 | 1.8 | 3.3 | 5.8 | 3.25 | 3.8 | 12 | 6.5 | M3 | √ | - | - | - | 1 | 100 | 0.08
KOR 1,5/4 (100 PCS) | E11KM-01020100560 |  |  |  |  | 4 | 4.8 | 13 |  | M4 | [6 empty] | 0.1
KOR 1,5/5 (100 PCS) | E11KM-01020100660 |  |  |  |  | 4.75 | 5.3 | 14 | 7.5 | M5 | [6 empty] | 0.09
KOR 1,5/6 (100 PCS) | E11KM-01020100760 |  |  |  |  | 6.5 | 6.3 | 16 | 9 | M6 | [6 empty] | 0.1
KOR 2,5/3 (100 PCS) | E11KM-01020100850 | 2.5 | 2.3 | 4.2 | 5.8 | 3.25 | 3.8 | 12 | 7.5 | M3 | √ | - | - | - | 1 | 100 | 0.13
KOR 2,5/4 (100 PCS) | E11KM-01020100950 |  |  |  |  | 4 | 4.8 | 13 |  | M4
KOR 2,5/5 (100 PCS) | E11KM-01020101050 |  |  |  |  | 4.75 | 5.3 | 14 | 8.5 | M5 | [6 empty] | 0.14
KOR 2,5/6 (100 PCS) | E11KM-01020101150 |  |  |  |  | 6.5 | 6.3 | 16 | 9.5 | M6 | [6 empty] | 0.16
KOR 2,5/8 (100 PCS) | E11KM-01020101220 |  |  |  |  | 7.75 | 9.3 | 20 | 13 | M8 | [6 empty] | 0.19
KOR 4/4 (100 PCS) | E11KM-01020101360 | 4 | 3 | 5 | 7.8 | 4.75 | 5.3 | 18 | 8.5 | M4 | √ | - | - | - | 1 | 100 | 0.22
KOR 4/5 (100 PCS) | E11KM-01020101450 | [5 empty] | 5.8 |  | 9 | M5
KOR 4/6 (100 PCS) | E11KM-01020101550 |  |  |  |  | 6.5 | 6.3 | 19 | 10 | M6 | [6 empty] | 0.26
KOR 4/8 (100 PCS) | E11KM-01020101650 |  |  |  |  | 8.5 | 9.3 | 22 | 13 | M8 | [6 empty] | 0.28

## Table 7
Date of publication: | 2025-03-07 | Graphic project, pictures and all technical data and descriptions in this catalogue are protected by Polish and international copyright laws. Names and logos used in the content of this catalogue may be trademarks, for which ZAE Ergom Sp. z o.o. has exclusive protection rights. ZAE ERGOM reserves the right for changes in the assortment and parameters of its products.

## Table 9
Type | Index Ergom | Cross-section, rm/sm [mm²] | d | D | a | c1 | c2 | E | W | Screw hole | UL | Socket code no. - 2 class | Socket code no. - 5 class | Lz/s | Lz/w | Quantity in package [pcs] | Weight [kg]
KOR 6/4 (100 PCS) | E11KM-01020101760 | 6 | 4 | 6 | 8.7 | 5 | 5.3 | 18 | 9.5 | M4 | √ | 4 | - | 1 | 1 | 100 | 0.3
KOR 6/5 (100 PCS) | E11KM-01020101850 |  |  |  |  | 6 | 5.8 | 19 |  | M5 | [6 empty] | 0.31
KOR 6/6 (100 PCS) | E11KM-01020101960 |  |  |  |  | 7 | 6.3 |  | 10 | M6 | [6 empty] | 0.35
KOR 6/8 (100 PCS) | E11KM-01020102060 |  |  |  |  | 8.5 | 9.3 | 22 | 14 | M8 | [6 empty] | 0.37
KOR 6/10 (100 PCS) | E11KM-01020102160 |  |  |  |  | 11 | 11.8 | 25 | 16 | M10 | [6 empty] | 0.4
KOR 6/12 (100 PCS) | E11KM-01020102250 |  |  |  |  | 12 | 12.8 |  | 19 | M12
KOR 10/5 (100 PCS) | E11KM-01020102300 | 10 | 4.5 | 7 | 10 | 7 | 7.5 | 21 | 12 | M5 | √ | 7 | FL10 | 1 | 1 | 100 | 0.53
KOR 10/6 (100 PCS) | E11KM-01020102400 | [5 empty] | 8 | 21.5 |  | M6 | [5 empty] | 100 | 0.52
KOR 10/8 (100 PCS) | E11KM-01020102500 |  |  |  |  | 9 | 10 | 23.5 | 15 | M8 | [5 empty] | 100 | 0.6
KOR 10/10 (100 PCS) | E11KM-01020102600 |  |  |  |  | 11 | 12 | 25.5 | 17 | M10 | [5 empty] | 100 | 0.65
KOR 10/12 (100 PCS) | E11KM-01020102700 |  |  |  |  | 12 | 13 | 26.5 | 19 | M12 | [5 empty] | 100 | 0.64
KOR 16/5 (100 PCS) | E11KM-01020102800 | 16 | 5.5 | 8.5 | 13 | 7 | 7.5 | 25 | 12 | M5 | √ | 8 | FL16 | 1 | 2 | 100 | 0.91
KOR 16/6 (100 PCS) | E11KM-01020102900 | [5 empty] | 8 | 25.5 |  | M6 | [5 empty] | 100 | 0.9
KOR 16/8 (100 PCS) | E11KM-01020103000 |  |  |  |  | 9 | 10 | 27.5 | 15 | M8 | [5 empty] | 100 | 0.97
KOR 16/10 (100 PCS) | E11KM-01020103100 |  |  |  |  | 11 | 12 | 29.5 | 17 | M10 | [5 empty] | 100 | 1
KOR 16/12 (100 PCS) | E11KM-01020103250 |  |  |  |  | 12 | 13 | 30.5 | 19 | M12 | [5 empty] | 100 | 1.1
KOR 25/5 (100 PCS) | E11KM-01020103300 | 25 | 7 | 10 | 15 | 7 | 7.5 | 28 | 14 | M5 | √ | 10 | FL25 | 1 | 2 | 100 | 1.18
KOR 25/6 (100 PCS) | E11KM-01020103400 | [5 empty] | 8 | 28.5 |  | M6 | [5 empty] | 100 | 1.22
KOR 25/8 (100 PCS) | E11KM-01020103500 |  |  |  |  | 9 | 10 | 30.5 | 16 | M8 | [5 empty] | 100 | 1.25
KOR 25/10 (100 PCS) | E11KM-01020103600 |  |  |  |  | 11 | 12 | 32.5 | 18 | M10 | [5 empty] | 100 | 1.3
KOR 25/12 (100 PCS) | E11KM-01020103700 |  |  |  |  | 12 | 13 | 33.5 | 19 | M12 | [5 empty] | 100 | 1.3
KOR 25/14 (100 PCS) | E11KM-01020103800 |  |  |  |  | 14 | 15 | 35.5 | 21 | M14 | [5 empty] | 100 | 1.45
KOR 35/5 (100 PCS) | E11KM-01020103880 | 35 | 8.5 | 12 | 17 | 7.5 | 8 | 31.5 | 18 | M5 | √ | 12 | FL35 | 1 | 2 | 100 | 1.6
KOR 35/6 (100 PCS) | E11KM-01020103900 |  |  |  |  | 7 |  |  |  | M6 | [5 empty] | 100 | 1.8
KOR 35/8 (100 PCS) | E11KM-01020104000 |  |  |  |  | 9 | 10 | 33.5 |  | M8 | [5 empty] | 100 | 1.94
KOR 35/10 (100 PCS) | E11KM-01020104100 |  |  |  |  | 11 | 12 | 35.5 |  | M10 | [5 empty] | 100 | 2.1
KOR 35/12 (100 PCS) | E11KM-01020104200 |  |  |  |  | 12 | 13 | 36.5 | 20 | M12 | [5 empty] | 100 | 2.05
KOR 35/14 (100 PCS) | E11KM-01020104300 |  |  |  |  | 14 | 15 | 38.5 | 21 | M14 | [5 empty] | 100 | 2.2
KOR 35/16 (100 PCS) | E11KM-01020104400 |  |  |  |  | 16 | 16 | 39.5 | 26 | M16 | [5 empty] | 100 | 2.3

## Table 10
Date of publication: | 2025-03-07 | Graphic project, pictures and all technical data and descriptions in this catalogue are protected by Polish and international copyright laws. Names and logos used in the content of this catalogue may be trademarks, for which ZAE Ergom Sp. z o.o. has exclusive protection rights. ZAE ERGOM reserves the right for changes in the assortment and parameters of its products.

## Table 11
Type | Index Ergom | Cross-section, rm/sm [mm²] | d | D | a | c1 | c2 | E | W | Screw hole | UL | Socket code no. - 2 class | Socket code no. - 5 class | Lz/s | Lz/w | Quantity in package [pcs] | Weight [kg]
KOR 50/6 (100 PCS) | E11KM-01020104500 | 50 | 10 | 14 | 19 | 7 | 8 | 34.5 | 20 | M6 | √ | 14 | FL50 | 1 | 2 | 100 | 2.58
KOR 50/8 (100 PCS) | E11KM-01020104600 |  |  |  |  | 9 | 10 | 36.5 |  | M8 | [5 empty] | 100 | 2.8
KOR 50/10 (100 PCS) | E11KM-01020104700 |  |  |  |  | 11 | 12 | 38.5 |  | M10 | [5 empty] | 100 | 3.05
KOR 50/12 (100 PCS) | E11KM-01020104800 |  |  |  |  | 12 | 13 | 39.5 | 23 | M12 | [5 empty] | 100 | 2.95
KOR 50/14 (100 PCS) | E11KM-01020104900 |  |  |  |  | 14 | 15 | 41.5 |  | M14 | [5 empty] | 100 | 3.2
KOR 50/16 (100 PCS) | E11KM-01020105000 |  |  |  |  | 16 | 16 | 42.5 | 28 | M16 | [5 empty] | 100 | 3.3
KOR 50/20 (100 PCS) | E11KM-01020105100 |  |  |  |  | 20 | 20.6 | 47 | 30 | M20 | [5 empty] | 100 | 3.6
KOR 70/6 (100 PCS) | E11KM-01020105200 | 70 | 12 | 16.5 | 21 | 9 | 10 | 40.5 | 23 | M6 | √ | 16 | FL70 | 1 | 2 | 100 | 4.25
KOR 70/8 (100 PCS) | E11KM-01020105300 | [8 empty] | M8 | [5 empty] | 100 | 4.2
KOR 70/10 (100 PCS) | E11KM-01020105400 |  |  |  |  | 12 | 13 | 43.5 |  | M10 | [5 empty] | 100 | 4.6
KOR 70/12 (100 PCS) | E11KM-01020105500 | [8 empty] | M12 | [5 empty] | 100 | 4.4
KOR 70/14 (100 PCS) | E11KM-01020105600 |  |  |  |  | 16 | 16 | 46.5 | 28 | M14 | [5 empty] | 100 | 4.9
KOR 70/16 (100 PCS) | E11KM-01020105700 | [8 empty] | M16 | [5 empty] | 100 | 4.7
KOR 70/20 (100 PCS) | E11KM-01020105800 |  |  |  |  | 20 | 20.6 | 51 | 31 | M20 | [5 empty] | 100 | 5
KOR 95/8 (50 PCS) | E11KM-01020105900 | 95 | 13.5 | 18 | 24 | 12 | 13 | 47 | 26 | M8 | √ | 17 | FL95 | 1 | 2 | 50 | 2.8
KOR 95/10 (50 PCS) | E11KM-01020106000 | [8 empty] | M10 | [5 empty] | 50 | 2.72
KOR 95/12 (50 PCS) | E11KM-01020106100 | [8 empty] | M12 | [5 empty] | 50 | 2.65
KOR 95/14 (50 PCS) | E11KM-01020106200 |  |  |  |  | 16 | 16 | 50 |  | M14 | [5 empty] | 50 | 2.85
KOR 95/16 (50 PCS) | E11KM-01020106300 | [7 empty] | 29 | M16 | [5 empty] | 50 | 2.85
KOR 95/20 (50 PCS) | E11KM-01020106400 |  |  |  |  | 20 | 20.6 | 54.5 | 35 | M20 | [5 empty] | 50 | 3.1
KOR 120/8 (50 PCS) | E11KM-01020106500 | 120 | 15 | 19.5 | 26 | 12 | 13 | 50 | 29 | M8 | √ | 19 | FL120 | 1 | 2 | 50 | 3.3
KOR 120/10 (50 PCS) | E11KM-01020106600 | [8 empty] | M10 | [5 empty] | 50 | 3.15
KOR 120/12 (50 PCS) | E11KM-01020106700 | [8 empty] | M12 | [5 empty] | 50 | 3.17
KOR 120/14 (50 PCS) | E11KM-01020106800 |  |  |  |  | 16 | 16 | 53 |  | M14 | [5 empty] | 50 | 3.4
KOR 120/16 (50 PCS) | E11KM-01020106900 | [8 empty] | M16 | [5 empty] | 50 | 3.4
KOR 120/20 (50 PCS) | E11KM-01020107000 |  |  |  |  | 20 | 20.6 | 57.5 | 35 | M20 | [5 empty] | 50 | 3.5

## Table 12
Date of publication: | 2025-03-07 | Graphic project, pictures and all technical data and descriptions in this catalogue are protected by Polish and international copyright laws. Names and logos used in the content of this catalogue may be trademarks, for which ZAE Ergom Sp. z o.o. has exclusive protection rights. ZAE ERGOM reserves the right for changes in the assortment and parameters of its products.

## Table 14
Type | Index Ergom | Cross-section, rm/sm [mm²] | d | D | a | c1 | c2 | E | W | Screw hole | UL | Socket code no. - 2 class | Socket code no. - 5 class | Lz/s | Lz/w | Quantity in package [pcs] | Weight [kg]
KOR 150/8 (50 PCS) | E11KM-01020107100 | 150 | 16.5 | 21 | 29 | 12 | 13 | 54 | 31 | M8 | √ | 20 | FL150 | 2 | 3 | 50 | 3.78
KOR 150/10 (50 PCS) | E11KM-01020107200 | [8 empty] | M10 | [5 empty] | 50 | 3.73
KOR 150/12 (50 PCS) | E11KM-01020107300 | [8 empty] | M12 | [5 empty] | 50 | 3.55
KOR 150/14 (50 PCS) | E11KM-01020107400 |  |  |  |  | 16 | 16 | 57 |  | M14 | [5 empty] | 50 | 3.9
KOR 150/16 (50 PCS) | E11KM-01020107500 | [8 empty] | M16 | [5 empty] | 50 | 3.8
KOR 150/20 (50 PCS) | E11KM-01020107600 |  |  |  |  | 20 | 20.6 | 61.5 | 35 | M20 | [5 empty] | 50 | 4.2
KOR 185/10 (50 PCS) | E11KM-01020107700 | 185 | 19 | 24 | 30 | 12 | 13 | 56.5 | 35 | M10 | √ | 23 | FL185 | 2 | 3 | 50 | 4.92
KOR 185/12 (50 PCS) | E11KM-01020107800 | [8 empty] | M12 | [5 empty] | 50 | 4.82
KOR 185/14 (50 PCS) | E11KM-01020107900 |  |  |  |  | 16 | 16 | 59.5 |  | M14 | [5 empty] | 50 | 5.35
KOR 185/16 (50 PCS) | E11KM-01020108000 | [8 empty] | M16 | [5 empty] | 50 | 5.11
KOR 185/20 (50 PCS) | E11KM-01020108100 |  |  |  |  | 20 | 20.6 | 64 | 38 | M20 | [5 empty] | 50 | 5.5
KOR 240/10 (50 PCS) | E11KM-01020108200 | 240 | 21 | 26 | 38 | 20 | 20.6 | 73.5 | 38 | M10 | √ | 25 | FL240 | 2 | 4 | 50 | 7.3
KOR 240/12 (50 PCS) | E11KM-01020108300 | [8 empty] | M12 | [5 empty] | 50 | 7.3
KOR 240/14 (50 PCS) | E11KM-01020108400 | [8 empty] | M14 | [5 empty] | 50 | 7.2
KOR 240/16 (50 PCS) | E11KM-01020108500 | [8 empty] | M16 | [5 empty] | 50 | 7.1
KOR 240/20 (50 PCS) | E11KM-01020108600 | [8 empty] | M20 | [5 empty] | 50 | 7
KOR 300/10 (25 PCS) | E11KM-01020108700 | 300 | 24 | 30 | 45 | 20 | 20.6 | 82.5 | 43 | M10 | − | 28 | FL300 | 2 | 6 | 25 | 5.7
KOR 300/12 (25 PCS) | E11KM-01020108800 | [8 empty] | M12 | [5 empty] | 25 | 5.5
KOR 300/14 (25 PCS) | E11KM-01020108900 | [8 empty] | M14 | [5 empty] | 25 | 5.55
KOR 300/16 (25 PCS) | E11KM-01020109000 | [8 empty] | M16 | [5 empty] | 25 | 5.5
KOR 300/20 (25 PCS) | E11KM-01020109100 | [8 empty] | M20 | [5 empty] | 25 | 5.2
KOR 400/12 | E11KM-01020109202 | 400 | 27.5 | 33.5 | 50 | 20 | 20.6 | 90 | 49 | M12 | − | 32 | - | 2 | - | 1 | 0.3
KOR 400/16 | E11KM-01020109402 | [8 empty] | M16
KOR 400/20 | E11KM-01020109502 | [8 empty] | M20
KOR 500/12 | E11KM-01020109602 | 500 | 31 | 38 | 70 | 20 | 20.6 | 112.5 | 55 | M12 | − | 36 | - | 3 | - | 1 | 0.5
KOR 500/14 | E11KM-01020109702 | [8 empty] | M14
KOR 500/16 | E11KM-01020109802 | [8 empty] | M16
KOR 500/20 | E11KM-01020109902 | [8 empty] | M20
KOR 625/12 | E11KM-01020110002 | 625 | 34 | 40 | 70 | 20 | 20.6 | 114 | 60 | M12 | − | 42 | - | 3 | - | 1 | 0.5
KOR 625/16 | E11KM-01020110202 | [8 empty] | M16
KOR 625/20 | E11KM-01020110302 | [8 empty] | M20
Lz/s - Number of crimping - wide, Lz/w - Number of crimping - narrow

## Table 15
Date of publication: | 2025-03-07 | Graphic project, pictures and all technical data and descriptions in this catalogue are protected by Polish and international copyright laws. Names and logos used in the content of this catalogue may be trademarks, for which ZAE Ergom Sp. z o.o. has exclusive protection rights. ZAE ERGOM reserves the right for changes in the assortment and parameters of its products.